## For Input
Insulation Resistance Measurement Input Sheet-For DEMO
Title | ○○Electric Equipment Modification Work (Electrical Equipment Work) |  |  |  |  | Judgement Criteria Voltage to Ground: Below 150V circuit |  | Above 0.1MΩ
Site place | Ueda, Nagano, 386-1111, Japan |  |  |  |  | Judgement Criteria Voltage to Ground: Above 150V, Below 300V circuit |  | Above 0.2MΩ
Measurement Date | 2020-10-19 |  |  |  |  | As an in-house standard, all new wiring has an insulation resistance value |  | Above 0.1MΩ
Temperature/Humidity | 26℃ 50%rh |  | Weather |  | Cloudy
Measured by | Name |  | Inspected by |  | Name
Instrument name | Insulation Tester
Model | IR4057-50 |  | Serial number |  | 200641846
Manufactured date | 2020-06-01 |  | Calibrated date |  | 2020-06-01
Manufacturer name | HIOKI E.E CORPORATION
Location | Circuit no. | Ref. value | Measurement place | Value（MΩ）
A Block Circuit Breaker A | L-A | 0.1 | R-E | 101 | M Ohm
|  |  | S-E | 101 | M Ohm
|  |  | T-E | 101 | M Ohm
|  |  | R-S | 66.4 | M Ohm |  | HIOKI disclaims any and all responsibility for any consequences arising out of use of this template.
|  |  | S-T | 99.9 | M Ohm
|  |  | T-R | 99.9 | M Ohm
B Block Circuit Breaker A | L-B | 0.1 | R-E | 102 | M Ohm
|  |  | S-E | 102 | M Ohm
|  |  | T-E | 99.8 | M Ohm
|  |  | R-S | 84.5 | M Ohm
|  |  | S-T | 99.9 | M Ohm
|  |  | T-R | 101 | M Ohm
B Block Circuit Breaker 2 | L-C | 0.1 | R-E | 0.01 | M Ohm
|  |  | S-E | 0.02 | M Ohm
|  |  | T-E | 0.03 | M Ohm
R-S
S-T
T-R
C Block Circuit Breaker 1 | C-01 | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
D Block Circuit Breaker C | C-02 | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
D Block Circuit Breaker D | C-03 | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
Pantry Circuit Breaker | A-7 | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
Lab A Circuit Breaker | C-A | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
Lab B Circuit Breaker | C-B | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
Lab C Circuit Breaker | C-C | 0.1 | R-E
S-E
T-E
R-S
S-T
T-R
Lab D Circuit Breaker | D-A | 0.2 | R-E
S-E
T-E
R-S
S-T
T-R
Street Lamp 1 Circuit Breaker | F-1 | 0.2 | R-E
S-E
T-E
R-S
S-T
T-R
Street Lamp 2 Circuit Breaker | F-2 | 0.2 | R-E
S-E
T-E
R-S
S-T
T-R

## For report
Submission date YYMMDD
Insulation Resistance Inspection
| Title | ○○Electric Equipment Modification Work (Electrical Equipment Work)
| Site place | Ueda, Nagano, 386-1111, Japan
| Measurement Date | 2020-10-19
| Temperature/Humidity | 26℃ 50%rh |  |  | Weather |  |  | Cloudy
| Measured by | Name |  |  | Inspected by |  |  | Name
| Instrument name | Name | Insulation Tester
|  | Model | IR4057-50
|  | Manufacturer | HIOKI E.E CORPORATION
|  | Manufactured date | 2020-06-01
|  | Serial No. | 200641846
|  | Calibrated date | 2020-06-01
| Location | Circuit No. | Measurement value（ＭΩ） | [5 empty] | Ref. Value | Judgement
|  |  | Ｒ－Ｅ | Ｓ－Ｅ | Ｔ－Ｅ | Ｒ－Ｓ | Ｓ－Ｔ | Ｔ－Ｒ | ＭΩ
| A Block Circuit Breaker A | L-A | 101 | 101 | 101 | 66.4 | 99.9 | 99.9 | 0.1 | Pass
| B Block Circuit Breaker A | L-B | 102 | 102 | 99.8 | 84.5 | 99.9 | 101 | 0.1 | Pass
| B Block Circuit Breaker 2 | L-C | 0.01 | 0.02 | 0.03 |  |  |  | 0.1 | Fail
| C Block Circuit Breaker 1 | C-01 | [6 empty] | 0.1 | Pass
| D Block Circuit Breaker C | C-02 | [6 empty] | 0.1 | Pass
| D Block Circuit Breaker D | C-03 | [6 empty] | 0.1 | Pass
| Pantry Circuit Breaker | A-7 | [6 empty] | 0.1 | Pass
| Lab A Circuit Breaker | C-A | [6 empty] | 0.1 | Pass
| Lab B Circuit Breaker | C-B | [6 empty] | 0.1 | Pass
| Lab C Circuit Breaker | C-C | [6 empty] | 0.1 | Pass
| Lab D Circuit Breaker | D-A | [6 empty] | 0.2 | Pass
| Street Lamp 1 Circuit Breaker | F-1 | [6 empty] | 0.2 | Pass
| Street Lamp 2 Circuit Breaker | F-2 | [6 empty] | 0.2 | Pass